## Sheet1
Fire Stopping Systems available on FPA Register
FIRESTOP CENTRE LTD (Distributor of PROTECTA, 3M, TRAFALGAR, CSD, ALLPROOF and TENMAT Brands)
Unit J / 657 Great South Rd
Penrose
AUCKLAND
09 4834000
info@firestopcentre.co.nz
https://www.firestopcentre.co.nz/
Service Penetration | Orientation | Substrate | System Description | FRR | System Dimensions | Report Ref. | System ID#
BLANKS
Blank | Floor | Concrete or Aerated Concrete | Protecta FR Board 60mm double-sided top and bottom of 150mm floor slab | -/180/120 | Max opening 2400mm x 1200mm | Warringtonfire FAS 200262 | FC256
Blank | Floor | Concrete or Aerated Concrete | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | -/120/90 | Max opening 2400mm x 1200mm | Warringtonfire FAS 200262 | FC257
Blank | Wall | Concrete, Aerated Concrete or Masonry from 75mm | 2 layers Protecta FR Board 60mm double-sided or 50mm 1-S | Up tp -/240/240 | Unlimited width, Max 1200mm high | Warringtonfire FAS 200262 | FC252
Blank | Wall | Concrete, Aerated Concrete or Masonry from 75mm | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | Up to -/240/90 | Unlimited width, Max 1200mm high | Warringtonfire FAS 200262 | FC253
Blank | Wall to Roof | Plasterboard or Concrete/AAC/Masonry | 1 layer Protecta FR Board 60mm double-sided friction fitted between top of wall and substrate above. | -/240/90 | Unlimited width, Max 1200mm high | Warringtonfire FAS 200262 | FC311
Blank | Wall | Plasterboard | Protecta FR Board 50mm single-sided flush with plasterboard each side of wall. | -/120/120 | Unlimited width, Max 1200mm high | Warringtonfire FAS 200262 | FC258
Blank | Wall | Plasterboard 13mm Single-layer | Protecta FR Acrylic Sealant 12.5mm each side, no backing required | -60/60 | Up to 150x150mm | Warringtonfire FAS190390 | FC329
Blank | Wall | Plasterboard 13mm Double-layer | Protecta FR Acrylic Sealant 12.5mm each side with stone wool backing | -120/120 | Up to 300x300mm | Warringtonfire FAS190390 | FC261
Blank | Floor | Concrete or Aerated Concrete | Protecta FR Acrylic Sealant 25mm top only or 15mm top and bottom with stone wool backing | Up to -/240/240 | Up to 300x300mm | Warringtonfire FAS190390 | FC262
Blank | Wall | Concrete or Aerated Concrete | Protecta FR Acrylic Sealant 12.5-25mm with stone wool backing | Up to -/240/240 | Up to 300x300mm | Warringtonfire FAS190390 | FC259
Blank | Floor | Concrete or Aerated Concrete 100mm | Protecta EX Mortar 50mm, backed with 50mm stone wool | -180/180 | Up to 2400x1200mm | Warringtonfire FAS 210027 | FC267
Blank | Floor | Concrete or Aerated Concrete | Protecta EX Mortar 100mm | -240/240 | Up to 2400x1200mm | Warringtonfire FAS 210027 | FC268
Blank | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 50mm, backed with 50mm stone wool | -180/120 | Up to 2400x1200mm | Warringtonfire FAS 210027 | FC264
Blank | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 100mm | -240/240 | Up to 2400x1200mm | Warringtonfire FAS 210027 | FC265
Blank | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Board 60mm to each side of the wall, pattress fitted | -240/180 | Up to 600x600mm | Warringtonfire FAS 200262 | FC255
Blank | Wall | Plasterboard | Protecta FR Collar to both sides of the wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC436
Blank | Floor | Concrete or Aerated Concrete | Protecta FR Collar to underside of floor | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC443
Blank | Floor | Concrete or Aerated Concrete | 3M Putty 40mm backed with mineral wool | -240/240 | Up to 100mm diam | CSIRO RIR FCO-3220 | FC283
Blank | Wall | Plasterboard | 3M Putty 20mm each side backed with mineral wool | -240/240 | Up to 100mm diam | CSIRO RIR FCO-3220 | FC284
Blank | Wall | Solid timber or CLT | Protecta FR Board, 50mm or 60mm to each side of wall. Pattress fit option also | -120/120 | Unlimited width, Max 1200mm high | Warringtonfire FAS 200262 | FC166
Blank | Wall | Naked NZS 3604 Timber Frame | Protecta FR Board, 50mm or 60mm to each side of wall. | -120/120 | Up to 600mm x 1200mm | Warringtonfire FAS 200262 | FC168
Blank | Wall | Plasterboard | Protecta FR Board 50mm single-sided flush with plasterboard each side of wall. | -/120/120 | Unlimited width, Max 1200mm high | Warringtonfire FAS 200262 | FC601
Blank | Floor | Solid Timber or CLT 150mm | Protecta FR Acrylic Sealant 25mm top and bottom with stone wool backing | -/120/120 | Up to 220mm diam | Warringtonfire FAS190390 | FC413
Blank | Wall | Solid Timber or CLT 100mm | Protecta FR Acrylic Sealant 25mm each side backed with stone wool | -/120/120 | Up to 180mm diam | Warringtonfire FAS190390 | FC135
NON-INSULATED METAL PIPES
Steel, Copper, Alupex | Wall | Plasterboard | Protecta FR Board 50mm single-sided flush with plasterboard each side of wall. | Up to -/120/30 | Steel to 324mm, Copper to 54mm, Alupex to 16mm | Warringtonfire FAS 200262 | FC313
Steel, Copper, Alupex | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Board 60mm double-sided flush with plasterboard each side of wall. | Up to -/240/- | Steel to 219mm, Copper to 54mm, Alupex to 16mm | Warringtonfire FAS 200262 | FC569
Steel, Copper or Alupex | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 15mm both sides | -/240/- | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC327
Steel, Copper or Alupex | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 25mm one side only | Up to -/240/- | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC328
Steel | Wall | Plasterboard 13mm single-layer | Protecta FR Acrylic Sealant 25mm one side only | -/60/30 | Up to 22mm diam | Warringtonfire FAS190390 | FC330
Steel, Copper or Alupex | Wall | Plasterboard | Protecta FR Acrylic Sealant 12.5mm each side | Up to -/120/- | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC333
Steel, Copper, Alupex | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 15-25mm one side only | Up to -/240/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC335
Steel, Copper, Alupex | Floor | Composite Concrete or Aerated Concrete | Protecta FR Acrylic Sealant 15-25mm with backing | Up to -/240/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC638
Steel or Copper | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 25mm both sides | Up to -/240/240 | Steel to 219mm, Copper to 54mm | Warringtonfire FAS190390 | FC300
Steel, Copper, Alupex | Floor | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 210027 | FC339
Steel, Copper, Alupex | Floor or Wall | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 100mm | Up to -/240/120 | Steel to 219mm, Copper to 54, Alupex 75mm | Warringtonfire FAS 210027 | FC340
Steel, Copper, Alupex | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/- | Steel to 219mm, Copper to 54, Alupex 75mm | Warringtonfire FAS 210027 | FC345
Steel, Copper, Alupex | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 100mm | -/240/120 | Steel to 219mm, Copper to 54, Alupex 75mm | Warringtonfire FAS 210027 | FC346
Steel, Copper, Ferrous | Wall | Plasterboard | 3M CP 25WB+ Sealant with 3M E-5A-4 Endothermic Mat for insulation rating | Up to -/120/120 | Steel to 114mm, Copper / Ferrous to 15mm | Exova RIR 23263-01 | FC350
Steel, Copper, Ferrous | Wall | Concrete, Aerated Concrete or Masonry | 3M CP 25WB+ Sealant with 3M E-5A-4 Endothermic Mat for insulation rating | Up to -/240/120 | Steel to 114mm, Copper / Ferrous to 15mm | Exova RIR 23263-01 | FC293
Steel, Copper or Alupex | Wall | Concrete, Aerated Concrete or Masonry | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | -/240/- | Steel to 325mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC351
Steel, Copper or Alupex | Wall | Plasterboard | Protecta FR Putty Cord fillet each side of wall (annular space can be zero) | Up to -/120/120 | Steel to 30mm, Copper to 12mm, Alupex to 20mm | Exova EWFA 53619700-A.4 | FC352
Steel, Copper or Alupex | Wall | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet each side of wall (annular space can be zero) | Up to -/120/121 | Steel to 30mm, Copper to 12mm, Alupex to 20mm | Exova EWFA 53619700-A.5 | FC404
Steel or Copper | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet to bottom side of floor only (annular space can be zero) | Up to -/120/120 | Steel to 30mm, Copper to 12mm | Exova EWFA 53619700-A.4 | FC357
Steel or Copper | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet to top side of floor only (annular space can be zero) | Up to -/120/120 | Steel to 22mm, Copper to 10mm | Exova EWFA 53619700-A.4 | FC358
Copper | Floor | Concrete or Aerated Concrete from 120mm | 3M Putty around pipe and top of floor | Up to -/120/90 | Copper up to 200mm | CSIRO RIR FCO-3220 | FC502
Copper | Wall | Concrete or Aerated Concrete from 100mm | 3M Putty around pipe and each side of wall | Up to -/120/90 | Copper up to 200mm | CSIRO RIR FCO-3220 | FC503
Copper | Wall | Plasterboard | 3M Putty around pipe and each side of wall | Up to -/120/90 | Copper up to 200mm | CSIRO RIR FCO-3220 | FC504
Steel, Copper or Alupex | Wall | Plasterboard | Protecta EX Mortar 25mm, backed with 50mm stone wool | Up to -/120/- | Copper up to 54mm, Steel to 219mm, Alupex to 75mm | Warringtonfire FAS 210027 | FC562
Steel | Floor | Concrete or Aerated Concrete from 120mm | 2 layers Protecta FR Board 60mm double-sided anywhere in the floor | Up to -/240/- | Up to 219mm diam | Warringtonfire FAS 200262 | FC573
Steel, Copper, Alupex | Floor | Concrete or Aerated Concrete from 100mm | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | Up to -/240/- | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC574
Steel, Copper, Alupex | Floor | Solid Timber or CLT 150mm | 1 layer Protecta FR Board 50mm or 60mm within aperture with second FR Board overlapping the aperture. | Up to -/90/- | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC578
Steel, Copper, Alupex | Wall | Concrete, Aerated Concrete or Masonry | 2 layers Protecta FR Board 60mm double-sided | Up to -/240/- | Steel to 219mm, Copper to 54mm, Alupex to 16mm | Warringtonfire FAS 200262 | FC569
Steel, Copper, Alupex | Wall | Solid Timber or CLT 100mm | Protecta FR Board 50mm or 60mm flush with each side of wall. | Up to -/120/30 | Steel to 324mm, Copper to 54mm, Alupex to 16mm | Warringtonfire FAS 200262 | FC591
Steel, Copper | Wall | Plasterboard | Protecta FR Collar to each side of wall. | Up to -/120/90 | Steel to 54mm, Copper to 54mm | Warringtonfire FAS 190125 | FC435
Steel, Copper | Wall | Solid Timber or CLT 100mm | Protecta FR Collar to each side of wall. | Up to -/120/90 | Steel to 54mm, Copper to 54mm | Warringtonfire FAS 190125 | FC609
Steel, Copper | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Collar to each side of wall. | Up to -/120/90 | Steel to 54mm, Copper to 54mm | Warringtonfire FAS 190125 | FC616
Steel, Copper or Alupex | Floor | Solid Timber or CLT miin 150mm | Protecta FR Acrylic Sealant 25mm top and bottom | Up to -/120/- | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC415
Steel, Copper or Alupex | Wall | Solid Timber or CLT 100mm | Protecta FR Acrylic Sealant 25mm each side with stone wool | -/90/- | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC314
Brass Wingback | Wall | Plasterboard Single Layer | Allproof Fire Rated Mastic MAS310 to full depth of lining | -/60/60 | Brass wingback 20mm od | BRANZ Appraisal 1008 | FC691
INSULATED METAL PIPES
Steel, Copper, Alupex (Interrupted Insulation) | Wall | Concrete, Aerated Concrete or Masonry | 2 layers Protecta FR Board 60mm double-sided | Up to -/240/180 | Steel to 219mm, Copper to 54mm, Alupex to 16mm | Warringtonfire FAS 200262 | FC177
Steel, Copper, Alupex (Continous or Interrupted) | Wall | Concrete, Aerated Concrete or Masonry | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | Up to -/240/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC178
Steel (Interrupted) | Floor | Concrete or Aerated Concrete from 120mm | 2 layers Protecta FR Board 60mm double-sided anywhere in the floor | Up to -/240/240 | Up to 219mm diam | Warringtonfire FAS 200262 | FC185
Steel, Copper, Alupex (Interrupted) | Floor | Concrete or Aerated Concrete from 100mm | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | Up to -/240/240 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC186
Steel, Copper, Alupex (Combustible insulation) | Floor | Concrete or Aerated Concrete from 120mm | 2 layers Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | Up to -/240/120 | Steel to 165mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC167
Steel, Copper, Alupex (Interrupted) | Floor | Solid Timber or CLT 150mm | 1 layer Protecta FR Board 50mm or 60mm within aperture with second FR Board overlapping the aperture. | Up to -/90/90 | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC577
Steel, Copper, Alupex (Continuous, Combustible) | Wall | Plasterboard | Protecta FR Board 50mm single-sided each side of wall, with Protecta FR Pipe Wrap. | Up to -/120/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC274
Steel, Copper, Alupex (Continuous, Combustible) | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Board 50mm single-sided each side of wall, with Protecta FR Pipe Wrap. | Up to -/120/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC234
Steel, Copper, Alupex (Continuous) | Wall | Plasterboard | Protecta FR Board 50mm single-sided flush with plasterboard each side of wall. | Up to -/120/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC272
Steel, Copper, Alupex (Interrupted) | Wall | Plasterboard | Protecta FR Board 50mm single-sided flush with plasterboard each side of wall. | Up to -/120/120 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC189
Steel, Copper, Alupex (Continuous) | Wall | Plasterboard | 1 Protecta FR Board 60mm double-sided anywhere in aperture | Up to -/90/60 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC171
Copper, Alupex (Combustible Ins) | Wall | Plasterboard | 1 Protecta FR Board 60mm double-sided anywhere in aperture with FR Collars | Up to -/60/60 | Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC170
Steel, Copper or Alupex (Interrupted) | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 25mm one side only | Up to -/240/240 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC116
Steel (Continuous) | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 25mm one side only | -/180/180 | Up to 324mm diam | Warringtonfire FAS190390 | FC278
Steel, Copper or Alupex (Interrupted) | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 15mm both sides | -/240/120 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC117
Steel, Copper, Alupex (Continuous) | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 15mm both sides | -/240/240 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC279
Steel, Copper, Alupex (Continuous, Combustible) | Wall | Concrete, Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 25mm both sides | Up to -/120/120 | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC324
Steel, Copper, Alupex (Combustible insulation) | Wall | Plasterboard | Protecta FR Acrylic Sealant 12.5mm both sides | -/120/90 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC119
Steel (Continuous) | Wall | Plasterboard, single layer | Protecta FR Acrylic Sealant 12.5mm both sides | -/60/45 | Steel to 324mm | Warringtonfire FAS190390 | FC331
Steel, Copper or Alupex (Interrupted) | Wall | Plasterboard | Protecta FR Acrylic Sealant 12.5mm both sides | Up to -/120/120 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC121
Steel, Copper or Alupex (Interrupted) | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 15-25mm one side only | Up to -/240/180 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC125
Steel, Copper or Alupex (Interrupted) | Floor | Composite Concrete or Aerated Concrete | Protecta FR Acrylic Sealant 15-25mm with backing | Up to -/240/180 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC637
Steel, Copper, Alupex (Continuous) | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 25mm top side only | -/240/240 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC302
Steel, Copper, Alupex (Continuous) | Floor | Composite floor min 73m topping | Protecta FR Acrylic Sealant 25mm top side only | -/240/240 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC260
Steel, Copper, Alupex (Continuous, Combustible) | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 25mm both sides | Up to -/180/120 | Steel to 165mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC299
Steel (Interrupted) | Floor | Concrete or Aerated Concrete from 70mm | Protecta FR Acrylic Sealant 15mm both sides | -/240/120 | Up to 219mm diam | Warringtonfire FAS190390 | FC298
Steel or Copper (Interrupted Insulation) | Floor | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/180 | Steel to 219mm diam, Copper to 54mm | Warringtonfire FAS 210027 | FC202
Steel (Continuous) | Floor | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/240/240 | Up to 324mm diam | Warringtonfire FAS 210027 | FC338
Steel (Interrupted) | Floor or Wall | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 100mm | Up to -/240/240 | Up to 219mm diam | Warringtonfire FAS 210027 | FC204
Steel, Copper, Alupex (Combustible insulation) | Floor or Wall | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 100mm with Protecta FR Pipe Wrap | Up to -/240/240 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 210027 | FC205
Steel (Continuous) | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 50mm, backed with 50mm stone wool | -/120/90 | Up to 219mm diam | Warringtonfire FAS 210027 | FC195
Steel, Copper, Alupex (Interrupted) | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/120 | Steel to219mm, Copper to 54mm, Alupex 75mm | Warringtonfire FAS 210027 | FC196
Steel (Continuous, Combustible) | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 100mm with Protecta FR Pipe Wrap | Up to -/240/60 | Up to 165mm diam | Warringtonfire FAS 210027 | FC344
Steel (Interrupted) | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 100mm | Up to -/240/240 | Up to 219mm diam | Warringtonfire FAS 210027 | FC199
Steel, Copper, Alupex (Combustible Ins) | Wall | Plasterboard | Protecta EX Mortar 50mm with 2 layers Protecta FR Pipe Wrap each side | Up to -/120/120 | Steel to 165mm, Copper to 54mm, Alupex to 75mm diam | Warringtonfire FAS 210027 | FC163
Steel, Copper or Alupex (Interrupted) | Wall | Plasterboard | Protecta EX Mortar 25mm each side, with stone wool backing | Up to -/120/120 | Steel to 219mm, Alupex to 75mm, Copper to 54mm | Warringtonfire FAS 210027 | FC212
Steel, Copper, Alupex (Continuous) | Wall | Concrete, Aerated Concrete or Masonry | 2 layers Protecta FR Board 60mm double-sided | Up to -/240/180 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC275
Steel or Copper (Interrupted) | Wall | Plasterboard | Protecta FR Putty Cord fillet each side of wall (annular space can be zero) | Up to -/120/120 | Steel to 324mm, Copper to 54mm | Exova EWFA 53619700-A.4 | FC353
Steel or Copper (Interrupted) | Wall | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet each side of wall (annular space can be zero) | Up to -/120/120 | Steel to 324mm, Copper to 54mm | Exova EWFA 53619700-A.5 | FC405
Steel or Copper (Continous Insulation) | Wall | Plasterboard | Protecta FR Putty Cord fillet each side of wall (annular space can be zero) | Up to -/120/120 | Steel to 324mm, Copper to 54mm | Exova EWFA 53619700-A.4 | FC354
Steel or Copper (Continous Insulation) | Wall | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet each side of wall (annular space can be zero) | Up to -/120/120 | Steel to 324mm, Copper to 54mm | Exova EWFA 53619700-A.5 | FC406
Steel or Copper (Interrupted) | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet to top side of floor only (annular space can be zero) | Up to -/240/240 | Steel to 324mm, Copper to 54mm | Exova EWFA 53619700-A.4 | FC359
Steel or Copper (Continous Insulation) | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord fillet to top side of floor only (annular space can be zero) | Up to -/240/240 | Steel to 324mm, Copper to 54mm | Exova EWFA 53619700-A.4 | FC360
Steel (Continuous, Combustible) | Wall | Concrete or Aerated Concrete from 100mm | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture, with wrap. | -/120/30 | Steel to 165mm | Warringtonfire FAS 200262 | FC363
Steel, Copper or Alupex (Combustible) | Wall | Plasterboard | Protecta FR Acrylic Sealant 25mm both sides | Up to -/120/120 | Steel to 165mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC365
Steel, Copper or Alupex (Combustible) | Wall | Plasterboard | Protecta Collar to each side of the wall | Up to -/120/90 | Steel/Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 190125 | FC437
Metal or Plastic (Continuous) | Floor | Concrete or Aerated Concrete from 100mm | Protecta Collar to underside of floor | Up to -/180/180 | Steel/Copper to 54mm, Alupex to 75mm, PP/PE to 160mm | Warringtonfire FAS 190125 | FC441
Copper (Continous Foam Insulation) | Wall | Plasterboard or Concrete | Protecta FR Pipe Wrap to each side of the wall | Up to -/120/120 | Up to 54mm diam | Warringtonfire FAS 200262 | FC364
Copper Pair Coil with FR insulation | Wall | Plasterboard or Concrete | Trafalgar FyrePEX sealant 25mm both sides | -/120/120 | Up to 110mm diam | BRANZ FAR 4849 | FC451
Copper Pair Coils with FR insulation | Wall | Concrete or Hebel PowerPanel | Trafalgar FyrePEX sealant 60mm from either side | -/90/90 | Up to 120mm diam | BRANZ FAR 4849 | FC452
Copper Pair Coils with FR insulation | Floor | Concrete | Trafalgar FyrePEX sealant 60mm from either side | -/120/120 | Up to 120mm diam | BRANZ FAR 4849 | FC453
Copper Pair Coils with PE foam insulation | Floor | Concrete | Trafalgar FyreCHOKE Collar to underside of floor | -/120/120 | Up to 80mm diam | CSIRO FSP 1709 | FC459
Copper Pair Coils with PE foam insulation | Wall | Plasterboard or Concrete | Trafalgar FyreCHOKE Collar to each side of the wall | Up to -/90/45 | Up to 80mm diam | CSIRO FSP 1801 | FC460
Copper Pair Coils with PE foam insulation | Wall | Hebel AAC panel wall | Trafalgar FyreCHOKE Collar to each side of the wall | -/90/60 | Up to 80mm diam | CSIRO FSP 1795 | FC462
Copper, Alupex with combustible insulation | Wall | Concrete, Aerated Concrete or Masonry | Single Protecta FR Board 60mm anywhere in aperture | Up to -/60/60 | Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC276
Steel, Copper or Alupex (Combustible) | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Wrap to both sides | Up to -/120/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC584
Steel, Copper or Alupex (Combustible) | Floor | Concrete, Aerated Concrete | Protecta FR Wrap to soffit side only | Up to -/180/120 | Steel to 165mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC575
Steel, Copper or Alupex (Continuous) | Wall | Solid timber or CLT miin 100mm | Protecta FR Board to both sides | Up to -/120/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC588
Steel, Copper or Alupex (Combustible) | Wall | Solid timber or CLT miin 100mm | Protecta FR Board to both sides with FR Wrap | Up to -/120/120 | Steel to 324mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC589
Steel, Copper or Alupex (Interrupted) | Wall | Solid timber or CLT miin 100mm | Protecta FR Board to both sides | Up to -/120/120 | Steel to 219mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 200262 | FC590
Metal or Plastic (Continuous) | Floor | Solid Timber or CLT miin 150mm | Protecta Collar to underside of floor | Up to -/180/180 | Steel/Copper to 54mm, Alupex to 75mm, PP/PE to 160mm | Warringtonfire FAS 190125 | FC596
Steel, Copper or Alupex (Combustible) | Wall | Solid timber or CLT miin 100mm | Protecta Collar to each side of the wall | Up to -/120/90 | Steel/Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 190125 | FC608
Steel, Copper or Alupex (Combustible) | Wall | Concrete, Aerated Concrete or Masonry from 100mm | Protecta Collar to each side of the wall | Up to -/120/90 | Steel/Copper to 54mm, Alupex to 75mm | Warringtonfire FAS 190125 | FC615
Steel, Copper or Alupex (Interrupted) | Floor | Solid Timber or CLT miin 150mm | Protecta FR Acrylic Sealant 25mm top and bottom | Up to -/120/120 | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC414
Steel, Copper or Alupex (Interrupted) | Wall | Solid timber or CLT miin 100mm | Protecta FR Acrylic Sealant 25mm each side wih stone wool | Up to -/90/90 | Steel to 273mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC137
Steel, Copper or Alupex (Combustible) | Wall | Solid timber or CLT miin 100mm | Protecta FR Acrylic Sealant 25mm each side wih stone wool | Up to -/60/45 | Steel to 114mm, Copper to 54mm, Alupex to 75mm | Warringtonfire FAS190390 | FC109
PLASTIC PIPES
PVC, PE, PP, PEX Pipes | Wall | Plasterboard Single Layer 13mm | Protecta Collar to each side of wall | Up to -/60/60 | Up to 160mm diam | Warringtonfire FAS 190125 | FC541
PVC, PE, PP, PEX Pipes | Wall | Plasterboard (100mm) | Protecta Collar to each side of wall | Up to -/120/120 | Up to 400mm diam | Warringtonfire FAS 190125 | FC144
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Protecta Collar to each side of wall | Up to -/240/240 | Up to 400mm diam | Exova EWFA 51478400-B.1 | FC145
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Single Protecta Collar to either side of wall | Up to -/240/180 | Up to 160mm diam | Exova EWFA 51478400-B.2 | FC550
PVC, PE, PP, PEX Pipes | Floor | Concrete or Aerated Concrete | Protecta Collar to underside of floor | Up to -/240/240 | Up to 400mm diam | Warringtonfire FAS 190125 | FC146
PVC, PE, PP, PEX Pipes | Floor | Concrete or Aerated Concrete 100mm | Protecta Collar to top side of floor | Up to -/240/240 | Up to 160mm diam | Warringtonfire FAS 190125 | FC444
PVC, PE, PP, PEX Pipes | Floor | Concrete or Aerated Concrete Composite Floor | Protecta Collar to top side of floor | Up to -/240/240 | Up to 160mm diam | Warringtonfire FAS 190125 | FC438
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic Sealant 25mm both sides | Up to -/240/240 | Up to 32mm diam | Warringtonfire FAS190390 | FC325
PVC, PE, PP, PEX Pipes | Floor | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 100mm with Protecta FR Pipe Wrap | Up to -/240/240 | Up to 250mm diam | Warringtonfire FAS 210027 | FC206
PEX Pipes | Wall | Plasterboard or Concrete | 3M 3000WT Sealant 26mm to both sides with 25mm fillet | -180/120 | Up to 25mm diam | Exova RIR 45239800.1 | FC282
PVC Pipes | Floor | Concrete or Aerated Concrete from 75mm | 3M Tuck-In Wrap Strips | Up to -/180/180 | Up to 160mm diam | BRANZ FC10453 | FC247
PVC Pipes | Wall | Plasterboard | 3M Tuck-In Wrap Strips | Up to -/120/120 | Up to 110mm diam | BRANZ FC10453 | FC288
PVC Pipes | Floor | Concrete or Aerated Concrete from 75mm | 3M Tuck-In Wrap Strips with 3M 3000WT Sealant to top of floor | Up to -/180/180 | Up to 160mm diam | BRANZ FC10453 | FC362
PVC Pipes | Wall | Concrete, Aerated Concrete or Masonry | 3M Tuck-In Wrap Strips one sided system with 3M IC15WB Sealant | Up to -/120/120 | Up to 110mm diam | BRANZ FC10453 | FC361
Reinforced PP Acoustic Pipes | Wall | Plasterboard | Protecta Collar to each side of the wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC432
PVC, PE, PP Pipes | Floor | Concrete from 100mm with timber formwork | Protecta Collar to underside of floor attached through timber formwork | Up to -/120/120 | Up to 160mm diam | Warringtonfire 51478400 | FC473
PEX, AluPEX Pipes | Floor | Concrete or Aerated Concrete from 120mm | Trafalgar FyrePEX sealant 60mm from either side | -/120/120 | 16mm | BRANZ FAR 4849 | FC454
PEX, AluPEX Pipes | Wall | Plasterboard or Concrete | Trafalgar FyrePEX sealant 25mm both sides | -/120/120 | PEX to 25mm. AluPex to 20mm | BRANZ FAR 4849 | FC455
PEX, AluPEX Pipes | Wall | Hebel or Concrete | Trafalgar FyrePEX sealant 60mm from either side | -/90/90 | PEX to 25mm. AluPex to 20mm | BRANZ FAR 4849 | FC456
PVC Pipe | Ceiling | Plasterboard | Trafalgar FyreCHOKE Collar on 60mm Maxilite Boatd | -/120/120 | Up to 50mm diam | Resolute TR-F49.01 | FC554
PP, HDPE, PEX Insulated Pipes | Floor/Wall | Concrete | Protecta EX Mortar 100mm with Protecta FR Pipe Wrap | Up to -/240/240 | Up to 260mm diam | Warringtonfire FAS 210027 | FC568
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Board and FR Wrap to each side of wall | Up to -/240/240 | Up to 400mm diam | Warringtonfire FAS 200262 | FC570
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Wrap to each side of wall with Acrylic Sealant | Up to -/240/240 | Up to 400mm diam | Warringtonfire FAS 200262 | FC571
PVC, PE, PP, PEX & Composite Pipes | Wall | Plasterboard | Protecta FR Board and FR Wrap to each side of wall | Up to -/120/120 | Up to 400mm diam | Warringtonfire FAS 200262 | FC581
PVC, PE, PP, PEX Pipes | Wall | Plasterboard | Single Protecta FR Board 2-S and Protecta FR Collar to each side of wall | Up to -/120/60 | Up to 160mm diam | Warringtonfire FAS 200262 | FC172
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Single Protecta FR Board 2-S and Protecta FR Collar to each side of wall | Up to -/120/60 | Up to 160mm diam | Warringtonfire FAS 200262 | FC104
PVC Pipes | Floor | Concrete, Aerated Concrete | Protecta FR Wrap to bottom side of floor | -/90/90 | Up to 110mm diam | Warringtonfire FAS 200262 | FC585
PVC, PE, PP, PEX & Composite Pipes | Wall | Solid timber or CLT 100mm | Protecta FR Board and FR Wrap to each side of wall | Up to -/120/120 | Up to 400mm diam | Warringtonfire FAS 200262 | FC593
PVC, PE, PP, PEX Pipes | Floor | Solid Timber or CLT 150mm | Protecta Collar to underside of floor | Up to -/240/240 | Up to 400mm diam | Warringtonfire FAS 190125 | FC147
PVC, PE, PP, PEX Pipes | Wall | Plasterboard | Protecta Collar to each side of the wall | -/90/90 | Pipes to 40mm in bundles up to 160mm diam | Warringtonfire FAS 190125 | FC598
PVC-U Pipes | Wall | Concrete, Aerated Concrete or Masonry | 3M Tuck-In Wrap Strips with 3M IC15WB or CP25WB Sealant to each side of wall | Up to -/120/120 | Up to 110mm diam | BRANZ FC10453 | FC087
PVC, PE, PP, PEX Pipes | Wall | Timber or CLT | Protecta Collar to each side of wall | Up to -/120/120 | Up to 400mm diam | Warringtonfire FAS 190125 | FC602
Reinforced PP Acoustic Pipes | Wall | Timber or CLT | Protecta Collar to each side of the wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC603
PVC, PE, PP, PEX Pipes | Wall | Timber or CLT | Protecta Collar to each side of the wall | -/90/90 | Pipes to 40mm in bundles up to 160mm diam | Warringtonfire FAS 190125 | FC604
Reinforced PP Acoustic Pipes | Wall | Concrete, Aerated Concrete or Masonry from 100mm | Protecta Collar to each side of the wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC610
PVC, PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry from 100mm | Protecta Collar to each side of the wall | -/90/90 | Pipes to 40mm in bundles up to 160mm diam | Warringtonfire FAS 190125 | FC611
PVC, PE, PP, PEX Pipes | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic sealant 25mm to top and bottom surface | Up to -/240/240 | PVC 50mm, PE 40mm, PP 75mm | Warringtonfire FAS190390 | FC617
PVC, PE, PP, PEX Pipes | Floor | Solid Timber or CLT 150mm | Protecta FR Acrylic sealant 25mm to top and bottom surface | Up to -/120/120 | PVC 32mm, PE 32mm, PP 32mm | Warringtonfire FAS190390 | FC416
PVC, PE, PP, PEX Pipes | Wall | Plasterboard Single Layer 13mm | Protecta FR Acrylic sealant 12.5mm each side | -/30/30 | PVC 32mm, PE 32mm, PP 32mm | Warringtonfire FAS190390 | FC418
PVC, PE, PP, PEX Pipes | Wall | Plasterboard | Protecta FR Acrylic sealant 25mm each side | Up to -/120/120 | PVC 32mm, PE 32mm, PP 32mm | Warringtonfire FAS190390 | FC618
PVC, PE, PP, PEX Pipes | Wall | Solid timber or CLT 100mm | Protecta FR Acrylic sealant 25mm each side | -/90/90 | PVC 32mm, PE 32mm, PP 32mm | Warringtonfire FAS190390 | FC108
PVC Pipes | Ceiling | Plasterboard 2 x 13mm | Allproof Drop-In Collar | -/90/90 | Up to 100mm diam | BRANZ Appraisal 1008 | FC634
PP-R, PP-MD Pipes | Floor | Concrete, Aerated Concrete from 70mm | Allproof Drop-In Collar | -/90/60 | Up to 150mm diam | BRANZ Appraisal 1008 | FC639
PVC Floor Waste | Floor | Concrete, Aerated Concrete from 70mm | Allproof Drop-In Collar | Up to -/120/120 | Up to 100mm diam | BRANZ Appraisal 1008 | FC635
PVC, HDPE, PP-MD Pipes | Floor | Composite Floor min topping 70mm | Allproof Drop-In Collar | Up to -/120/120 | Up to 150mm diam | BRANZ Appraisal 1008 | FC688
PVC Floor Waste | Floor | Composite Floor min topping 70mm | Allproof Drop-In Collar | Up to -/120/120 | Up to 100mm diam | BRANZ Appraisal 1008 | FC687
PVC, HDPE, PP-R, PP-MD Pipes | Floor | Concrete, Aerated Concrete from 120mm | Allproof Pipe Wraps | Up to -/120/120 | Up to 150mm diam | BRANZ Appraisal 1008 | FC671
PVC Floor Waste | Floor | Concrete, Aerated Concrete from 70mm | Allproof Low Profile Collar | Up to -/120/120 | Up to 100mm diam | BRANZ Appraisal 1008 | FC629
PVC Floor Waste | Floor | Concrete, Rib and Timber Infill from 70mm | Allproof Low Profile Collar | Up to -/120/120 | Up to 100mm diam | BRANZ Appraisal 1008 | FC734
PVC Pipe | Floor | Concrete, Rib and Timber Infill from 70mm | Allproof Low Profile Collar | Up to -/120/120 | Up to 100mm diam | BRANZ Appraisal 1008 | FC690
PVC, PE, PP, PEX Pipes | Floor | Concrete Hollow Core 150mm | Allproof Low Profile Collar | Up to -/90/90 | Up to 150mm diam | BRANZ Appraisal 1008 | FC730
PVC Floor Waste | Floor | Concrete Hollow Core 150mm | Allproof Low Profile Collar | Up to -/90/90 | Up to 100mm diam | BRANZ Appraisal 1008 | FC731
PVC, PE, PP, PEX Pipes | Ceiling | Plasterboard 2 x 13mm | Allproof Low Profile Collar | -/90/90 | Up to 100mm diam | BRANZ Appraisal 1008 | FC735
PVC Floor Waste | Ceiling | Plasterboard 2 x 13mm | Allproof Low Profile Collar | -/90/- | Up to 100mm diam | BRANZ Appraisal 1008 | FC736
PVC, PE, PP, PEX Pipes | Wall | Plasterboard Single Layer 13-19mm | Allproof Low Profile Collar | Up to -/120/120 | Up to 150mm diam | BRANZ Appraisal 1008 | FC737
PVC, PE, PP, PEX Pipes | Wall | Plasterboard Single Layer 13-19mm | Allproof Low Profile Collar inserted inside the wall | Up to -/120/90 | Up to 100mm diam | BRANZ Appraisal 1008 | FC738
PVC, PE, PP, PEX Pipes | Wall | Plasterboard Double Layer 13-16mm | Allproof Low Profile Collar | Up to -/120/120 | Up to 150mm diam | BRANZ Appraisal 1008 | FC742
PVC, PE, PP, PEX Pipes | Floor | Concrete, Aerated Concrete from 70mm | Allproof Low Profile Collar | Up to -/240/240 | Up to 150mm diam | BRANZ Appraisal 1008 | FC732
PVC, PEX, PEX/AL/PEX Pipes | Wall | Plasterboard Double Layer 13-16mm | Trafalgar FyreCHOKE Collar to both sides of wall | Up to -/120/120 | PVC up to 100mm, PEX, PEX/AL/PEX up to 25mm | BRANZ FAR FC11190 | FC525
PVC, PEX, PEX/AL/PEX Pipes | Wall | Concrete, Masonry, Hebel, Speedwall | Trafalgar FyreCHOKE Collar to both sides of wall | Up to -/120/120 | PVC up to 100mm, PEX, PEX/AL/PEX up to 25mm | BRANZ FAR FC11190 | FC527
PVC, PEX, PEX/AL/PEX Pipes | Floor | Concrete or Aerated Concrete from 120mm | Trafalgar FyreCHOKE Collar to underside of floor | Up to -/120/120 | PVC up to 100mm, PEX, PEX/AL/PEX up to 25mm | BRANZ FAR FC11190 | FC534
INSULATED PLASTIC PIPES
PE, PP, PEX Pipes | Wall | Plasterboard | Protecta FR Board and FR Wrap to each side of wall | -/60/60 | Up to 160mm diam | Warringtonfire FAS 200262 | FC364
PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Board and FR Wrap to each side of wall | -/60/60 | Up to 160mm diam | Warringtonfire FAS 200262 | FC103
PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Wrap to each side of wall | -/60/60 | Up to 160mm diam | Warringtonfire FAS 200262 | FC583
PE, PP, PEX Pipes | Wall | Solid timber or CLT 100mm | Protecta FR Board and FR Wrap to each side of wall | -/60/60 | Up to 160mm diam | Warringtonfire FAS 200262 | FC594
PE, PP, PEX Pipes | Wall | Plasterboard | Protecta FR Collar to each side of wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC599
PE, PP, PEX Pipes | Wall | Solid timber or CLT 100mm | Protecta FR Collar to each side of wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC607
PE, PP, PEX Pipes | Wall | Concrete, Aerated Concrete or Masonry from 100mm | Protecta FR Collar to each side of wall | Up to -/120/120 | Up to 160mm diam | Warringtonfire FAS 190125 | FC614
ELECTRICAL PENETRATION SERVICES
Cables - single, bundled, trays, conduits | Wall | Concrete, Aerated Concrete or Masonry | 2 layers Protecta FR Board 60mm double-sided | Up to -/180/120 | Cables to 80mm, Bundles to 100mm | Warringtonfire FAS 200262 | FC175
Cables - single, bundled, trays, conduits | Floor | Concrete or Aerated Concrete from 120mm | Protecta FR Board 60mm double-sided to top and bottom of 150mm floor slab | Up to -/120/120 | Cables to 80mm, Bundles to 100mm | Warringtonfire FAS 200262 | FC182
Cables - single, bundled, trays, conduits | Floor | Concrete or Aerated Concrete from 60mm | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | Up to -/90/30 | Cables to 80mm, Bundles to 100mm | Warringtonfire FAS 200262 | FC183
Cables - single, bundled, trays | Floor | Solid timber or CLT 150mm | 1 layer Protecta FR Board within aperture and second later overlapping the aperture. | Up to -/90/60 | Cables to 80mm, Bundles to 100mm | Warringtonfire FAS 200262 | FC576
Cables - single, bundled, trays, conduits | Wall | Plasterboard | 1 layer Protecta FR Board 50mm single-sided flush with plasterboard each side of wall | -/60/60 | Cables single or bundled to 80mm | Warringtonfire FAS 200262 | FC188
Cables - single or bundled | Wall | Plasterboard | 1 layer Protecta FR Board 50mm single-sided flush with plasterboard each side of wall | -/60/60 | Cables single or bundled to 100mm | Warringtonfire FAS 200262 | FC580
Cables - single | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic to one side of wall or anywhere inbetween | Up to -/240/120 | Single cable up to 21mm | Warringtonfire FAS190390 | FC113
Cables - single or bundled | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Acrylic to both sides of wall | Up to -/240/240 | Cables to 80mm, Bundles to 100mm | Warringtonfire FAS190390 | FC114
Cables - single or bundled | Wall | Plasterboard from single-layer 13mm | Protecta FR Acrylic Sealant to each side of wall | Up to -/60/45 | Cables to 21mm, Bundles to 100mm | Warringtonfire FAS190390 | FC174
Cables - single or bundled | Wall | Plasterboard single-layer 13mm, one side only | Protecta FR Acrylic Sealant to one side only of wall | Up to -/60/45 | Cables to 21mm, Bundles to 100mm | Warringtonfire FAS190390 | FC341
Cables - single or bundled | Wall | Plasterboard | Protecta FR Acrylic Sealant to each side of wall | Up to -/120/120 | Cables to 80mm, Bundles to 100mm | Warringtonfire FAS190390 | FC118
Cable single | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 25mm to top of floor | -/120/90 | Cable up to 21mm | Warringtonfire FAS190390 | FC123
Cable single | Floor | Composite from 50mm topping | Protecta FR Acrylic Sealant 25mm to top of floor | -/120/90 | Cable up to 21mm | Warringtonfire FAS190390 | FC636
Cables - single or bundled | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic Sealant 15mm to top and bottom of floor | Up to -/120/120 | Single or bundled cables up to 80mm diam | Warringtonfire FAS190390 | FC124
Cables - single or bundled | Floor | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/180 | Single or bundled cables up to 21mm diam, conduits | Warringtonfire FAS 210027 | FC201
Cables - single or bundled | Floor or Wall | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 100mm | Up to -/180/180 | Single or bundled cables up to 80mm diam, conduits | Warringtonfire FAS 210027 | FC337
Cables - trays | Floor | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/60 | Single or bundled cables up to 80mm diam | Warringtonfire FAS 210027 | FC336
Cables - trays | Floor or Wall | Concrete or Aerated Concrete from 100mm | Protecta EX Mortar 100mm | Up to -/180/60 | Single or bundled cables up to 80mm diam, conduits | Warringtonfire FAS 210027 | FC203
Cables - single or bundled, conduits | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/90 | Single or bundled cables up to 21mm diam, conduits | Warringtonfire FAS 210027 | FC194
Cables - trays | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 50mm, backed with 50mm stone wool | Up to -/180/60 | Single or bundled cables up to 80mm diam | Warringtonfire FAS 210027 | FC342
Cables - single or bundled, conduits | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 100mm | Up to -/240/240 | Single or bundled cables up to 80mm diam, conduits | Warringtonfire FAS 210027 | FC197
Cables - trays | Wall | Concrete, Aerated Concrete or Masonry | Protecta EX Mortar 100mm | -/240/60 | Single or bundled cables up to 80mm diam on trays | Warringtonfire FAS 210027 | FC343
Cables - single, bundles, trays, conduits | Wall | Plasterboard or Concrete from 100mm | Protecta EX Mortar 25mm each side, backed with mineral wool | Up to -/120/120 | Single or bundled cables up to 80mm diam, conduits | Warringtonfire FAS 210027 | FC211
Conduit | Wall | Plasterboard | 3M IC 15WB+ Sealant 26mm each side | Up to -/180/90 | Conduits up to 26mm | Exova RIR 45239800a.1 | FC347
Cables - single | Wall | Plasterboard | Protecta FR Putty Cord to both sides of wall | Up to -/120/120 | Single cables up to 80mm diam | Exova EWFA 53619700-A.5 | FC312
Cables - bundles | Wall | Plasterboard or Concrete from 100mm | Protecta FR Putty Cord to both sides of wall | Up to -/120/120 | Cable bundles up to 50mm | Exova EWFA 53619700-A.5 | FC349
Conduit, empty or up to 4 fibre optic cables | Wall | Plasterboard, concrete, masonry or AAC | 3M Ultra GS Wrap and 3M Mouldable Putty both sides of wall | -/120/120 | Conduits up to 26mm | CSIRO FCO-3220 | FC285
Cables D1 and D2 including cable trays | Wall | Plasterboard, concrete or masonry | 3M CP 25WB+ Sealant with 3M E-5A-4 Endothermic Mat for insulation rating | Up to -/120/120 | All D1 and D2 cables, including trays | Exova RIR 23263-01 | FC217
Cables D1 and D2 including cable trays | Floor | Concrete or Aerated Concrete from 120mm | 3M CP 25WB+ Sealant with 3M E-5A-4 Endothermic Mat for insulation rating | Up to -/180/120 | All D1 and D2 cables, including trays | Exova RIR 23263-01 | FC216
Cables - single | Wall | Concrete, Aerated Concrete or Masonry from 75mm | 1 layer Protecta FR Board 60mm double-sided positioned anywhere in the aperture. | -/240/90 | Single cable up to 21mm | Warringtonfire FAS 200262 | FC176
Cables - bundles - and Conduits | Wall | Concrete, Aerated Concrete or Masonry | 2 layers Protecta FR Board 60mm double-sided | Up to -/180/180 | Single or bundled cables up to 80mm diam, conduits | Warringtonfire FAS 200262 | FC310
Cables - single, bundled, trays, conduits | Wall | Concrete, Aerated Concrete or Masonry | Protecta FR Board 60mm to each side of the wall, pattress fitted | Up to -/240/180 | Single or bundled cables up to 80mm diam | Warringtonfire FAS 200262 | FC181
Cables - single or bundled | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord to top of floor only | Up to -/240/240 | Single or bundled cables up to 50mm diam | Exova EWFA 53619700-A.5 | FC355
Cables - single or bundled | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord to bottom of floor only | Up to -/120/60 | Single or bundled cables up to 75mm diam | Exova EWFA 53619700-A.5 | FC356
Cables - single or bundled | Wall | Concrete or Aerated Concrete from 100mm | Protecta FR Putty Cord to each side of the wall | Up to -/120/60 | Single or bundled cables up to 80mm diam | Exova EWFA 53619700-A.5 | FC403
Cables - single or bundled | Wall | Plasterboard from 100mm | Protecta FR Collar to both sides of wall | -/120/60 | Cable bundles up to 160mm | Warringtonfire FAS 190125 | FC434
Cables - single or bundled | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Collar to underside of floor only | Up to -/180/180 | Cable bundles up to 160mm | Warringtonfire FAS 190125 | FC442
Downlight | Ceiling | Plasterboard | Trafalgar FyreHAT inserted into ceiling | Up to -/120/90 | Downlights through apertures up to 105mm | CSIRO FSP 1290B | FC448
Conduit, empty or filled with cables | Wall | Plasterboard or Concrete from 100mm | Protecta FR Acrylic sealant 25mm to both sides of wall | Up to -/120/120 | Conduits up to 40mm | Warringtonfire FAS190390 | FC468
Conduit, empty or filled with cables | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Acrylic sealant 25mm to top and bottom surface | Up to -/240/240 | Conduits up to 40mm | Warringtonfire FAS190390 | FC466
Conduit, empty or filled with cables | Wall | Concrete from 100mm | Protecta FR Acrylic sealant 25mm to both sides of wall | Up to -/120/120 | Conduits up to 40mm | Warringtonfire FAS190390 | FC467
Conduit, empty or filled with cables | Wall | Plasterboard single layer 13mm | Protecta FR Acrylic sealant 25mm to both sides of wall | Up to -/60/45 | Conduits up to 32mm | Warringtonfire FAS190390 | FC469
Cables bundled, Pair Coil | Ceiling | Plasterboard | Trafalgar FyreBOX Maxi inserted into ceiling with Maxilite Board on bottom side | -/120/120 | Power or data cable bundles, pair coil | Resolute TR-F49.01 | FC555
Cables bundled, Pair Coil | Ceiling | Plasterboard | Trafalgar FyreBOX Mini inserted into ceiling with Maxilite Board on top side | -/120/120 | Power or data cable bundles, pair coil | Resolute TR-F49.01 | FC556
Conduits, fully or partially filled | Wall | Plasterboard or Concrete from 75mm | Protecta FR Board and FR Wrap each side of wall | -/120/90 | Conduits up to 110mm, cables up to 14mm | Warringtonfire FAS 200262 | FC559
Conduits, fully or partially filled | Wall | Concrete, Aerated Concrete or Masonry from 75mm | Protecta FR Board and FR Wrap each side of wall | -/120/90 | Conduits up to 110mm, cables up to 14mm | Warringtonfire FAS 200262 | FC102
Conduits, fully or partially filled | Floor/Wall | Concrete from 100mm | Protecta EX Mortar 100mm with Protecta FR Pipe Wrap | Up to -/120/120 | Conduits up to 110mm, cable bundles up to 90mm | Warringtonfire FAS 210027 | FC567
Conduits, fully or partially filled | Wall | Concrete from 100mm | Protecta FR Pipe Wrap 2 laters each side of wall | Up to -/120/90 | Conduits up to 110mm inc bundles | Warringtonfire FAS 200262 | FC101
Cables - single or bundled | Wall | Solid timber or CLT from 100mm | Protecta FR Board each side of wall | Up to -/120/120 | Single or bundled cables up to 100mm diam | Warringtonfire FAS 200262 | FC586
Cables - single, bundled, trays, conduits | Wall | Solid timber or CLT from 100mm | 1 layer Protecta FR Board 50mm single-sided flush with wall each side | Up to -/120/90 | Cables single or bundled to 80mm | Warringtonfire FAS 200262 | FC587
Conduits, fully or partially filled | Wall | Solid timber or CLT from 100mm | Protecta FR Board and FR Wrap each side of wall | -/120/90 | Conduits up to 110mm, cables up to 14mm | Warringtonfire FAS 200262 | FC592
Conduits, fully or partially filled | Floor | Concrete or Aerated Concrete from 100mm | Protecta FR Collar to underside of floor | -/90/90 | Conduit bundles up to 160mm | Warringtonfire FAS 190125 | FC440
Conduits, fully or partially filled | Floor | Solid timber or CLT from 150mm | Protecta FR Collar to underside of floor | -/90/90 | Conduit bundles up to 160mm | Warringtonfire FAS 190125 | FC439
Cables - bundled | Floor | Solid timber or CLT from 150mm | Protecta FR Collar to underside of floor | Up to -/180/180 | Cable bundles up to 160mm | Warringtonfire FAS 190125 | FC595
Conduits, fully or partially filled | Wall | Plasterboard from 100mm | Protecta FR Collar to both sides of wall | -/90/90 | Conduit bundles up to 160mm | Warringtonfire FAS 190125 | FC597
Cables - single or bundled | Wall | Solid timber or CLT from 100mm | Protecta FR Collar to both sides of wall | -/120/60 | Cable bundles up to 160mm | Warringtonfire FAS 190125 | FC605
Conduits, fully or partially filled | Wall | Solid timber or CLT from 100mm | Protecta FR Collar to both sides of wall | -/90/90 | Conduit bundles up to 160mm | Warringtonfire FAS 190125 | FC606
Cables - single or bundled | Wall | Concrete or Aerated Concrete from 100mm | Protecta FR Collar to both sides of wall | -/120/60 | Cable bundles up to 160mm | Warringtonfire FAS 190125 | FC612
Conduits, fully or partially filled | Wall | Concrete or Aerated Concrete from 100mm | Protecta FR Collar to both sides of wall | -/90/90 | Conduit bundles up to 160mm | Warringtonfire FAS 190125 | FC613
Cables - single or bundled | Floor | Solid timber or CLT from 150mm | Protecta FR Acrylic Sealant 25mm to top and bottom of floor | Up to -/120/120 | Single cables to 50mm or bundles up to 100mm diam | Warringtonfire FAS190390 | FC411
Cables - single or bundled | Wall | Solid timber or CLT from 100mm | Protecta FR Acrylic Sealant 25mm to each side of wall | Up to -/90/90 | Single cables to 50mm or bundles up to 100mm diam | Warringtonfire FAS190390 | FC136
Cables - single or bundled | Ceiling | Plasterboard 2x13mm | Allproof Low Profile Collar to underside of floor-ceiling system | -/90/90 | Cables and Pair Coils | BRANZ Appraisal 1008 | FC631
Cables - single or bundled | Wall | Plasterboard Single Layer 13mm | Allproof Low Profile Collar each side of wall | Up to -/60/60 | Cables, Conduits and Pair Coils | BRANZ Appraisal 1008 | FC632
Pair Coils | Wall | Plasterboard Single Layer 13mm | Allproof Low Profile Collar each side of wall, inserted inside wall | Up to -/60/60 | Cables, Conduits and Pair Coils | BRANZ Appraisal 1008 | FC633
Conduits with cables | Wall | Plasterboard, from Single Layer 13mm | Trafalgar FyreCHOKE Collar each side of wall | Up to -/120/120 | Conduit, rigid or flexible, up to 50mm | BRANZ FAR FC11190 | FC522
Conduits with cables | Wall | Concrete, Masonry, Hebel, Speedwall | Trafalgar FyreCHOKE Collar each side of wall | Up to -/120/120 | Conduit, rigid or flexible, up to 50mm | BRANZ FAR FC11190 | FC523
Conduits with cables | Floor | Concrete or Aerated Concrete from 120mm | Trafalgar FyreCHOKE Collar to underside of floor | Up to -/120/120 | Conduit, rigid or flexible, up to 50mm | BRANZ FAR FC11190 | FC524
Multiple Conduits with cables | Floor | Concrete or Aerated Concrete from 150mm | Trafalgar FyreCHOKE Collar to underside of floor | Up to -/180/180 | Multiple Conduits, rigid or flexible, up to 25mm | BRANZ FRT 210260 | FC740
SEISMIC/CONSTRUCTION JOINTS
Wall joints or Top of Wall to Floor above | Wall | Plasterboard, single layer 13mm | Protecta FR Acrylic Sealant to each side of wall | -/60/45 | Gaps/Joints up to 25mm | Warringtonfire FAS190390 | FC110
Wall joints or Top of Wall to Floor above | Wall | Plasterboard, double layer 13mm | Protecta FR Acrylic Sealant to each side of wall | -/90/90 | Gaps/Joints up to 25mm | Warringtonfire FAS190390 | FC506
Wall joints or Top of Wall to Floor above | Wall | Concrete, Aerated Concrete or Masonry from 75mm | Protecta FR Acrylic Sealant to each side of wall or one side only | Up to -/240/240 | Gaps/Joints up to 50mm | Warringtonfire FAS190390 | FC111
Linear joint seal in concrete floor slabs | Floor | Concrete, Aerated Concrete or Masonry from 100mm | Protecta FR Acrylic Sealant to top side of floor | Up to -/240/240 | Gaps/Joints up to 100mm | Warringtonfire FAS190390 | FC112
Wall joints or Top of Wall to Floor above | Wall | Plasterboard | Protecta FR Acrylic Sealant to each side of wall | Up to -/120/120 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC296
Wall joints or Top of Wall to Floor above | Wall | Concrete, Aerated Concrete or Masonry from 75mm | Protecta FR Acrylic Sealant to each side of wall | Up to -/240/240 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC322
Linear joint seal in concrete floor slabs | Floor | Concrete, Aerated Concrete or Masonry from 100mm | Protecta FR Acrylic Sealant to top and bottom of floor | -/180/180 | Gaps/Joints up to 100mm | Warringtonfire FAS190390 | FC323
Linear joint seal to timber | Wall | Plasterboard or concrete seal to timber | Protecta FR Acrylic Sealant to one or both sides of wall | Up to -/90/60 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC470
Linear joint seal steel to steel | Wall | Plasterboard or concrete seal to steel | Protecta FR Acrylic Sealant to one side only of wall | Up to -/120/30 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC472
Linear joint seal Concrete to steel | Wall | Concrete seal to steel framing | Protecta FR Acrylic Sealant both sides of wall | Up to -/120/60 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC563
Linear joint seal in Timber or CLT | Floor | Solid Timber or CLT | Protecta FR Board in gap and pattress-fitted to soffit | -/90/90 | Gaps/Joints up to 400mm | Warringtonfire FAS 200262 | FC549
Linear joint seal in concrete floor slabs | Floor | Concrete, Aerated Concrete or Masonry from 100mm | Protecta FR Acrylic Sealant to top and bottom of floor | -/240/120 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC412
Wall joints or Top of Wall to Floor above | Wall | Plasterboard, double layer 13mm | Protecta FR Acrylic Sealant to each side of wall | -/120/120 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC507
Linear joint to steel column | Wall | Plasterboard or concrete seal to steel | Protecta FR Acrylic Sealant to each side of wall | -/120/60 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC510
Linear joint to steel beam | Wall | Plasterboard or concrete seal to steel | Protecta FR Acrylic Sealant to each side of wall | -/120/60 | Gaps/Joints up to 30mm | Warringtonfire FAS190390 | FC508
Ventilated Cavity | Wall | Concrete, AAC, Masonry, Timber | Tenmat FF102 Strip | Up to -/120/120 | Gap up to 50mm | Warringtonfire WF428733 | FC739
Linear joint seals | Wall | Concrete, AAC, Masonry | Protecta FR IPT Sealant to each side of wall | Up to -/120/120 | Gap up to 30mm | UL International (UK) Ltd 4788415167 | FC540
HVAC
Ducts, Horizontal or Vertical | N/A | Open spaces or through any non fire-rated construction | 3M Duct Wrap 615+ Single Layer | -/120/120 | Ducts up to 1250 x 1000mm | BRANZ FAR4812 | FC232
Ducts, Horizontal, Internal Fire | Wall | Plasterboard, Concrete, AAC, Speedpanel | 3M Duct Wrap 615+ Single Layer | 60/60/60 | Ducts up to 3600 x 3600mm | CSIRO FCO-3273 | FC499
Ducts, Internal or External Fire | Wall | Plasterboard | 3M Duct Wrap 615+ Single Layer | 120/120/120 | Ducts up to 1250 x 1000mm | CSIRO FCO-3273 | FC230
Ducts, Internal or External Fire | Wall | Concrete, AAC, Speedpanel | 3M Duct Wrap 615+ Single Layer | 120/120/120 | Ducts up to 1250 x 1200mm | CSIRO FCO-3273 | FC498
Ducts, External Fire | Floor | Concrete | 3M Duct Wrap 615+ Single Layer | -/120/120 | Ducts up to 1250 x 1000mm | BRANZ FAR4812 | FC231
Ducts, Internal Fire | Floor | Concrete | 3M Duct Wrap 615+ Single Layer | 120/120/120 | Ducts up to 3600 x 3600mm | CSIRO FCO-3273 | FC501
Ducts, Internal or External Fire | Floor | Concrete | Protecta FR Damper | Up to -/180/120 | Ducts up to 1000mm, round or rectangular | Warringtonfire FAS190052 | FC474
Ducts, Internal or External Fire | Wall | Concrete | Protecta FR Damper | Up to -/120/120 | Ducts up to 1250mm round, 1700x1200mm rectangular | Warringtonfire FAS190052 | FC475
Ducts, Internal or External Fire | Wall | Plasterboard | Protecta FR Damper | Up to -/120/120 | Ducts up to 1250mm round, 1700x12500mm rectangular | Warringtonfire FAS190052 | FC477
Ducts, Internal or External Fire | Floor | Concrete | Protecta FR Damper | Up to -/180/120 | Ducts up to 1000mm, round | Warringtonfire FAS190052 | FC514
Ducts, Internal or External Fire | Floor | Concrete | Protecta FR Damper | Up to -/180/120 | Ducts up to 1000mm, round | Warringtonfire FAS190052 | FC515
Ducts, Internal or External Fire | Wall | Plasterboard | Trafalgar FyreWrap Plasterboard Wall | Up to -/120/120 | Ducts up to 1200 x 1200mm | BRANZ FAR4205 | FC494
Ducts, Internal or External Fire | Floor | Concrete | Trafalgar FyreWrap Concrete Floor | Up to -/120/120 | Ducts up to 1200 x 1200mm | BRANZ FAR4206 | FC497
Ducts, Internal or External Fire | Wall | Concrete, AAC, Speedpanel or Hebel | Trafalgar FyreWrap Concrete Wall | Up to -/120/120 | Ducts up to 1200 x 1200mm | CSIRO FCO3226 | FC496
HATCHES
Inspection Hatch | Ceiling | Plasterboard from single layer 13mm | FSC Fire-rated Inspection Hatch - no framing required. All ceilings up to 60mins | Up to 60/60/60 | 300mm x 300mm | BRANZ FAR4709 | FC493
Access Panel | Duct | HVAC Ducts | Trafalgar Duct Access Panel | 120/120/120 | Up to 710mm x 560mm | CSIRO FCO3226 | FC505
FLUSH BOXES / SOCKET BOXES
Flush boxes - single or back-to-back | Wall | Plasterboard from single layer 13mm | Protecta FR Putty Pad fitted to interior of box | Up to -/90/90 | Up to 100mm diam | Exova EWFA 53619700-A.2 | FC152
Flush boxes - single, double, back-to-back | Wall | Plasterboard from single layer 13mm | Allproof Intumescent Pad | Up to -/120/90 | Up to double box 130mm x 70mm | BRANZ Appraisal 1008 | FC630
MULTIPLE PENETRANTS
Cables, Pipes, Trays, Paircoils | Floor | Concrete from 120mm | Trafalgar FyreBOX Maxi, Mini or Cast-In | Up to -/240/240 | Multiple penetrants through gaps up to 1250mm | BRANZ FC10266 | FC511
Cables, Pipes, Trays, Paircoils | Wall | Plasterboard, concrete, AAC, Speedpanel | Trafalgar FyreBOX Maxi, Mini or Slab-mount | Up to -/120/120 | Multiple penetrants through gaps up to 1250mm | BRANZ FC10266 | FC512
Cables, Pipes, Trays, Paircoils | Wall | Plasterboard, concrete, AAC, Speedpanel | Trafalgar FyreBOX Maxi, Mini or Slab-mount | Up to -/120/120 | Multiple penetrants through gaps up to 1250mm | BRANZ FC10266 | FC513
Cables, Pipes, Trays, Paircoils | Floor | Concrete from 120mm | Trafalgar FyreBOX Mini | Up to -/240/240 | Multiple penetrants | BRANZ FC10266 | FC516
Cables, Pipes, Trays, Paircoils | Wall | Plasterboard, concrete, AAC, Speedpanel | Trafalgar FyreBOX Mini | Up to -/120/120 | Multiple penetrants | BRANZ FC10266 | FC517
STEEL BEAMS & COLUMNS
Universal Beams | Steelwork | N/A | Trafalgar COREX Board single or double layer | Up to 180/180/180 | All sizes of Universal Beams | Warringtonfire FAS 200445 | FC557
Universal Columns | Steelwork | N/A | Trafalgar COREX Board single or double layer | Up to 180/180/180 | All sizes of Universal Columns | Warringtonfire FAS 200445 | FC558